Slow control of the RPC gas system

Changguo  Lu, Princeton University

(January 21, 2009)

During a previous slow control phone meeting, some concerns were raised:

- Uncertainty of the COM port assignment through USB hub;

- Assign a serial number for each bubbler readout board to avoid the possible confusion;

- Technical feasibility of using LabView framework for the digital bubbler system.

Following are the answers to these questions.

- To save the number of cables between host PC and the digital bubbler readout crate we have adopted a method of using USB Hub/USB to RS232 converter cable. On the readout board site we use a 7-port USB Hub, through the USB to RS232 converter cable connecting to each board. From host PC to bubbler readout crate the cable routing path may need more than 20m long. Due to the limit of USB cable length is ~5m, we add a pair of USB extender at each end of a 100ft long CAT-5e cable, which is used to connect the pair of the USB extenders. So far this configuration has been tested at Princeton and IHEP,  it works quite stable.

The assignment of COM ports in this configuration can be adjusted via Device Manager in Windows. The readout board has LED installed in the front panel. If there is any communication between board and host PC, these LED will be flashing. This feature makes the COM ports assignment straight forward. The Bubbler GUI can check the communication board by board. After all COM ports are set up through Device Manager, run the Bubbler GUI, check the Communication, you will find the COM port assignment by noticing which board is flashing the LED. If there is wrong assignment you can use Device Manager to correct it right away. Upon finishing this initial assignment, all COM port # are permanently defined. Afterward you can reboot the PC, unplug the USB cable, then plug it back to the same USB slot, plug additional USB devices into the PC in different USB slots, etc. the COM ports used for the bubbler boards won’t be affected. They will keep the initial assigned number. The one to one correlation between COM port and readout board is fixed.

To be sure if this is the case, we have tested a system at Princeton. We checked the assignment of COM ports under various scenarios, we didn’t find any exception. The initial assignment has never been changed. We also called the USB Hub manufacture on this issue. Their technical support person stated that if you plug back the USB cable to the same USB slot, the COM port assignment should stay unchanged.

The concern reminds us we should add these comments into the gas system user’s manual, especially remind users always plug back the USB cable to the same slot if the cable has ever been unplugged for any reason.

- Although there is no need to worry about the mis-assignment of the COM port to the readout board, for further ease of the bubbler system initialization we are working on the GUI to assign a serial number to each board as a double assurance to the data integrity. After this assignment the serial number will be left on the information memory of MSP430 chip, w/o special permission it won’t be erased or changed. This serial number will be given to MySQL database. This work is in progress.

- IHEP slow control group has expressed their overall stratigies for the slow control system: they tend to put all subsystems under the LabView framework. This certainly will ease the future maintenance of the slow control system. But as Yinghong correctly pointed out the digital bubbler readout system is not just a simple data I/O port. To make this option feasible, the most important technical issue is the LabView API-DLL for the TI MSP430 microcontroller. TI does not provide this software support, some third party product has to be purchased. At Princeton we have found a commercial product “GangPro430 Programmer” is just suitable for this purpose. We are using it to check the performance of the readout board. Through either JTAG or BSL connection GangPro430 can have full control of up to 6 target devices (in our application the target device means readout board).

The following 2 excerpts from GangPro430 user’s manual should give you a glance of what this device can establish.

It seems to me is sufficient for writing a GUI with LabView. Each set of GangPro430/GangSplitter costs ~$300. Since we have 7 boards for near hall, 11 boards for far hall, each hall needs 2 sets of GangPro430, total six of them are needed.

This device uses JTAG or BSL connection to communicate with the target device, the present readout board has RS232 connector, so if we choose this option certain modification for the board is needed.

Attached below you can find its user’s manual (double click on the icon, the user’s manual will be displayed). The company’s web site is www.elprotronic.com.

There are a lot of similar third party products exsting on the market, the GangPro430 is just one of them. Elprotronic also opens sales office in China.

- Baseline design of the RPC gas slow control system

- Except the digital bubbler readout, all other on-line monitoring for the gas system can be merged to the LabView framework;

- The present Princeton digital bubbler readout GUI has been tested for some time, it is stable and reliable. Slow control can obtain all measured bubbling rates and channel numbers through MySQL database and display the data on their GUI, we suggest this should be the baseline system for now;

- Weather station is a commercial product, which provides its own software to display the various ambient weather parameters and record them into the data file. This device can be easily connect to the digital bubbler host PC via RS232 port. Dong Guan University will provide the hardware for temperature, atmospheric pressure and humidity measurement, to avoid the duplication I don’t think there is a need to send the weather station information to slow control. I rather prefer to put this device as a standalone device, record the weather information in its own PC as a double check to Dong Guan University’s measurement provided later on there is such request;

- The provided information for GangPro430 is FYI, if you are interested in developing the LabView GUI for the digital bubbler system, the tool is available.